**SURGE PROTECTION DEVICE.**

**UL 1449 4TH EDITION LISTED, TYPE 1, IN = 10 KA. INSTALL EXTERNAL TO GEAR WITH INTEGRAL CABLE. NEMA 4/12 ENCLOSURE. SURGE CURRENT RATING TO BE A TESTED VALUE. 10 YEAR WARRANTY. WITH STATUS LIGHTS. INSTALLED TESTING WITH A PORTABLE SURGE GENERATOR-TEST SET. RECORD ALL LET-THRU VOLTAGES. SUBMIT A REPORT TO THE ENGINEER. CURRENT TECHNOLOGY CGC SERIES.**