**SURGE PROTECTION DEVICE.**

**UL 1449 4TH EDITION LISTED, TYPE 1, IN = 20 KA. INSTALL EXTERNAL TO GEAR. NEMA 4/12 ENCLOSURE. SURGE CURRENT RATING TO BE A TESTED VALUE. 15 YEAR WARRANTY. STATUS LIGHTS, SURGE COUNTER AND FORM C CONTACTS. INSTALLED TESTING WITH A PORTABLE SURGE GENERATOR-TEST SET. RECORD ALL LET-THRU VOLTAGES. SUBMIT A REPORT TO THE ENGINEER. CURRENT TECHNOLOGY CGP SERIES.**