**SURGE PROTECTION DEVICE.**

**UL 1449 4TH EDITION LISTED, TYPE 1, IN = 20 KA (for CG-40, IN = 10 KA). INSTALL EXTERNAL TO GEAR. NEMA 4/12 ENCLOSURE. SURGE CURRENT RATING TO BE A TESTED VALUE. 10 YEAR WARRANTY. STATUS LIGHTS AND FORM C CONTACTS. INSTALLED TESTING WITH A PORTABLE SURGE GENERATOR-TEST SET. RECORD ALL LET-THRU VOLTAGES. SUBMIT A REPORT TO THE ENGINEER. CURRENT TECHNOLOGY CG SERIES.**