**POWERSMITHS ESAVER-25H SERIES.**

**UL 1561 LISTED. K-13 RATING. LOCKING HINGED DOORS. CU PRIMARY/AL SECONDARY, 105o C RISE. IMPEDANCES 4.0%-5.8%. SIX 2 ½% VOLTAGE TAPS (2 ABOVE, 4 BELOW). SOUND LEVELS 3DB LESS THAN NEMA ST-20. 25% LESS LOSSES AT APPLICABLE LOADING. 20% CONTINUOUS OVERLOAD CAPABILITY. INSTALLATION TO WITHIN 2” OF REAR SURFACE. GUARANTEED COMPATIBILITY WITH 125% RATED UPSTREAM CIRCUIT BREAKER. PROVIDE ENERGY SAVINGS & PAYBACK CALCULATION AGAINST US DOE 2016 X-FMRS. PROVIDE A COPY OF ISO 17025 REGISTRATION. PROVIDE INTEGRAL LOAD POWER AND ENERGY DATA LOGGER WITH EXTERNAL USB ACCESS TO DATA. PROVIDE TEST REPORT, BY SERIAL NUMBER, OF EACH TRANSFORMER SUPPLIED WITH SOUND LEVEL AND NO LOAD LOSS PERFORMANCE. 32 YEAR WARRANTY.**