**EXTERNALLY MOUNTED SPD. UL 1449 LISTED. NEMA 4/12. SINGLE-PULSE SURGE CURRENT CAPACITY: 60 KA/MODE, TO BE A TESTED VALUE. 10 YEAR WARRANTY. STATUS LIGHTS, FORM C CONTACTS AND AUDIBLE ALARM. WITH COMMISSIONING AND INSTALLED TESTING WITH PORTABLE SURGE GENERATOR-TEST SET. SUBMIT REPORT WITH LET-THRU VOLTAGES TO THE ENGINEER. CURRENT TECHNOLOGY CG-060 SERIES.**